## Cover
Cisco × NVIDIA HGX B300 — System Reference
OEM system options for the High-end tier · Xeon 6-hosted designs · Compiled 25 September 2026
Attribute | Value | Tag | Source
GPU | NVIDIA HGX B300 | [I]
Tier | High-end | [D]
System(s) | C880A M8 | [I]
Host socket / series | C880A M8: LGA-4710 (Xeon 6700P (Granite Rapids)) | [D]
GPU silicon reference | NVIDIA_B300_Reference.xlsx | [D]
Host CPU reference | Intel_Xeon6_Workload_SKU_Recommendations.xlsx rows 71-82 (see 5_Host_CPU_Map) | [I] | X5
Cross-OEM comparison | NVIDIA_Enterprise_GPU_Index.xlsx | [D]
POSITIONING
Cisco's only Xeon-hosted HGX platform: 10RU, 8× B300 with per-GPU CX-8, sold as fixed bundles (B301-B304) with Intersight management. B303 pairs 2× 6776P — workbook row 82 'Best'.
Power at a glance (live links to 4_Power_Budget)
Scenario | Est. max DC load (W) | PSU redundant output (W) | Status
B303 bundle · 12× 3200 W 54 V (6+6 assumed) | 12039.5 | 19200 | OK within redundant capacity
B303 bundle · 12× 3200 W (10+2 assumed) | 12039.5 | 32000 | OK within redundant capacity
Provenance discipline
Tag | Meaning | Confidence | Use in planning
[I] | Vendor-published (NVIDIA datasheet/product page, OEM spec sheet, QuickSpecs, product guide) | High | Plan against
[D] | Derived here by stated arithmetic from [I] values (formula visible in cell) | Medium-High | Use; check formula
[3P] | Third-party measurement, reseller listing or press arithmetic | Medium | Cross-check before bid
[U] | Unpublished / unverified / planning assumption (editable input) | Low | Replace with OEM calculator output
[N] | Not applicable / not supported | - | -

## 1_System_Spec
1 · System specifications
One block per chassis. Conflicts between sources are shown side-by-side, not resolved silently.
C880A M8 (Cisco)
System | Section | Parameter | Value | Tag | Src
C880A M8 | Identity | Model | Cisco UCS C880A M8 Rack Server (UCSC-C880A-M8) | [I] | C1
C880A M8 | Identity | Form factor | 10RU rack server, air-cooled (NetBox catalog lists 8U - conflict) | [I] | C1, C3
C880A M8 | Identity | Bundles | UCSC-880A-M8-B301 / -B302 / -B303 / -B304 with auto-included components | [I] | C1
C880A M8 | Processor | CPU | Two 6th Gen Intel Xeon (Granite Rapids); B303 bundle: 2× Xeon 6776P | [I] | C1, C2
C880A M8 | Memory | Slots / max | Up to 32 DDR5-6400 DIMMs; up to 4 TB (32× 128 GB) | [I] | C1
C880A M8 | GPU | Complex | 8× NVIDIA HGX B300 NVL8 (air-cooled 8-GPU board UCSAI-NVHGX-B300A); 2.3 TB HBM total | [I] | C1
C880A M8 | Network | E-W | 8× integrated NVIDIA ConnectX-8 (one per GPU) | [I] | C1
C880A M8 | Network | N-S | 4× PCIe Gen5 x16 FHHL; B303 includes 2× ConnectX-7 2×200G (crypto) | [I] | C1
C880A M8 | Network | LAN | 1× OCP 3.0 TFF Gen5 x8 NIC (CPU1) with 2× 10GbE RJ-45 (Intel X710-T2L) | [I] | C1
C880A M8 | Storage | Data cache | Up to 8× PCIe Gen5 x4 E1.S NVMe | [I] | C1
C880A M8 | Storage | Boot | Up to 2× 960 GB M.2 SATA with Cisco boot-optimised M.2 RAID controller | [I] | C1
C880A M8 | Power | PSUs | 12× 54 V 3200 W (UCSAI-PSU-3200W) | [I] | C1
C880A M8 | Cooling | Fans | 20× hot-swappable, N+1 | [I] | C1
C880A M8 | Management | BMC | Host BMC via DC-SCM with RJ45; IPMI 2.0, KVM, watchdog | [I] | C1
C880A M8 | Physical | Weight | 130 kg (catalog) | [3P] | C3
C880A M8 | Software | Options | NVIDIA AI Enterprise software and Cisco optics PIDs orderable | [I] | C1
C880A M8 | This workbook | GPU population | NVIDIA HGX B300 — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]

## 2_Components
2 · Component and option list
Part / feature codes as published. Max qty is per system. Use for BOM drafting; confirm in OEM configurator.
System | Subsystem | Component | Part / feature code | Max qty | Spec | Tag | Src | Note
C880A M8 | Base | C880A M8 8×B300, 2× 6776P, 8× CX-8, 2× CX-7, 4 TB | UCSC-880A-M8-B303 | 1 | Bundle | [I] | C1
C880A M8 | GPU | UCS C880A M8 GPU SLED B300 | UCSAI-880A-B3-SLD | 1 |  | [I] | C1
C880A M8 | GPU | NVIDIA HGX B300 Air-cooled 8-GPU Board | UCSAI-NVHGX-B300A | 1 |  | [I] | C1
C880A M8 | CPU | UCS C880A M8 CPU SLED | UCSAI-880A-CC-SLD | 1 |  | [I] | C1
C880A M8 | CPU | Intel GNR 6776P | UCSAI-CPU-I6776P | 2 | 64C 350 W | [I] | C1 | Workbook row 82
C880A M8 | CPU | Intel GNR heatsink | UCSAI-880A-HS | 2 |  | [I] | C1
C880A M8 | Memory | 128GB DDR5-6400 RDIMM 2Rx4 (32Gb) | UCSAI-MR128G2RG5 | 32 |  | [I] | C1
C880A M8 | Network | NVIDIA ConnectX-7 2×200G (crypto) | UCSAI-P-N7CS200GF | 2 |  | [I] | C1
C880A M8 | Network | OCP Intel X710-T2L | UCSAI-O-ID10GC | 1 |  | [I] | C1
C880A M8 | Network | Dual CX-7 bracket | UCSAI-2CX7200-BKT | 1 |  | [I] | C1
C880A M8 | Storage | 3.84TB E1.S Micron Gen5 NVMe | UCSAI-NVES3T8M1V | 2 | up to 8 | [I] | C1
C880A M8 | Boot | 960GB M.2 SATA Micron | UCSAI-M2-960G | 2 |  | [I] | C1
C880A M8 | Boot | M.2 RAID controller + carrier | UCSAI-M2-HWRAID / UCSAI-M2-CARRIER | 1 |  | [I] | C1
C880A M8 | Power | UCSAI M8 PSU 3200W 54V | UCSAI-PSU-3200W | 12 |  | [I] | C1
C880A M8 | Management | C880A M8 DC-SCM | UCSAI-880A-DCSCM | 1 |  | [I] | C1

## 3_Power_Rules
3 · OEM-published power and PSU rules
These constrain the scenarios on 4_Power_Budget. [U] rows are gaps to close with the OEM.
System | Rule | Tag | Src
C880A M8 | 12× 54 V 3200 W PSUs; redundancy scheme not in retrieved excerpt | [I] | C1
C880A M8 | 20 fans N+1 hot-swap | [I] | C1

## 4_Power_Budget
4 · Node power budget and rack fit (live model)
Blue-on-yellow cells are inputs. Component load is compared with PSU OUTPUT capacity in redundant mode; AC input and rack fit use PSU efficiency. Replace [U] inputs with OEM calculator output before any facility commitment.
Input | Unit | B303 bundle · 12× 3200 W 54 V (6+6 assumed) | B303 bundle · 12× 3200 W (10+2 assumed) | Tag | Basis
System |  | C880A M8 | C880A M8
GPUs installed | count | 8 | 8 | [I] | OEM max / scenario choice
GPU max power | W | 1100 | 1100 | [I] | NVIDIA / OEM GPU TDP
CPUs | count | 2 | 2 | [I] | OEM spec
CPU TDP | W | 350 | 350 | [I] | Scenario SKU choice - see 5_Host_CPU_Map
DIMMs | count | 32 | 32 | [I] | Scenario choice (max per 1_System_Spec)
Power per DDR5 RDIMM | W | 10 | 10 | [U] | Planning assumption; replace with OEM calculator
Data drives (NVMe) | count | 2 | 2 | [I] / [U] | Scenario choice
Power per data drive | W | 20 | 20 | [U] | Planning assumption: Gen5 U.2/E3.S ≈25 W, E1.S ≈20 W
Boot drives (M.2) | count | 2 | 2 | [I] | OEM spec
Power per boot drive | W | 5 | 5 | [U] | Planning assumption
Add-in NICs / DPUs | count | 3 | 3 | [I] / [U] | Scenario choice (N-S and/or E-W add-in)
Power per NIC / DPU | W | 25 | 25 | [U] | Planning assumption: CX-7 class ≈25 W; BlueField-3 ≈75 W
Baseboard / PCIe switch / NVSwitch / on-board CX-8 overhead | W | 1000 | 1000 | [U] | Planning placeholder - largest uncertainty on HGX nodes
Fans, VRs and conversion overhead | % of component load | 10% | 10% | [U] | Planning assumption
PSU efficiency at operating load | fraction | 0.95 | 0.95 | [U] | 80 PLUS Titanium ≈94-96% (HPE states up to 96%)
PSU output rating at site input voltage (0 = unpublished) | W | 3200 | 3200 | [I] | OEM spec
PSUs installed | count | 12 | 12 | [I] | OEM spec / scenario
PSUs held for redundancy | count | 6 | 2 | [U] | N+1 = 1, N+N = half
PSUs in dedicated GPU power domain (0 = not modelled) | count | 0 | 0 | [I] | HPE DL380a only
Rack power budget | kW | 30 | 30 | [U] | Your facility figure
Node height | RU | 10 | 10 | [I] | OEM spec
Usable rack units for compute | RU | 38 | 38 | [U] | 42U minus ToR, PDU, patch
Outputs (formulas)
Output | Unit | B303 bundle · 12× 3200 W 54 V (6+6 assumed) | B303 bundle · 12× 3200 W (10+2 assumed) | Tag | Formula basis
GPU load | W | 8800 | 8800 | [D] | GPUs × GPU W
CPU load | W | 700 | 700 | [D] | CPUs × TDP
Memory load | W | 320 | 320 | [D] | DIMMs × W
Storage load | W | 50 | 50 | [D] | drives × W + boot × W
Network add-in load | W | 75 | 75 | [D] | NICs × W
Baseboard / switch overhead | W | 1000 | 1000 | [D] | input
Component subtotal | W | 10945 | 10945 | [D] | sum of above
Fans / VR / conversion | W | 1094.5 | 1094.5 | [D] | subtotal × %
Estimated max DC load | W | 12039.5 | 12039.5 | [D] | subtotal + fans
GPU share of DC load | % | 73.09% | 73.09% | [D] | GPU ÷ DC
Estimated max AC input | W | 12673.1579 | 12673.1579 | [D] | DC ÷ efficiency
PSU output in redundant mode | W | 19200 | 32000 | [D] | (installed − redundant) × rating
Headroom (redundant) | W | 7160.5 | 19960.5 | [D] | capacity − DC load
PSU utilisation (redundant) | % | 62.71% | 37.62% | [D] | DC ÷ capacity
Redundancy check |  | OK within redundant capacity | OK within redundant capacity | [D]
GPU-domain PSU output (no domain redundancy) | W | n/a | n/a | [D] | GPU-domain PSUs × rating
GPU-domain check |  | n/a | n/a | [D] | GPU load ≤ domain output
Heat load | BTU/hr | 43240.8147 | 43240.8147 | [D] | AC W × 3.412
AC power per GPU (all-in) | kW | 1.5841 | 1.5841 | [D] | AC ÷ GPUs
Nodes per rack - power limited | count | 2 | 2 | [D] | rack W ÷ node AC
Nodes per rack - space limited | count | 3 | 3 | [D] | usable RU ÷ node RU
Nodes per rack | count | 2 | 2 | [D] | min(power, space)
GPUs per rack | count | 16 | 16 | [D] | nodes × GPUs
Rack AC load at that fit | kW | 25.3463 | 25.3463 | [D] | nodes × AC
Estimate is a planning ceiling at nameplate GPU/CPU power, not a measured draw. Sustained inference typically runs below nameplate; training and burn-in approach it. PSU ratings are OUTPUT watts at the stated input voltage - check derates (e.g., Dell 3200 W → 2900 W at 200-220 VAC; Lenovo 3200 W is 230 V-only).

## 5_Host_CPU_Map
5 · Host CPU map against the Xeon 6 SKU workbook
Rows 71-82 of 'SKU Recommendations' (GPU host CPU). Socket is the first filter; OEM qualified list the second.
C880A M8 — socket LGA-4710; series Xeon 6700P (Granite Rapids); OEM-qualified: 6776P
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
C880A M8 | Row 71 | Training | Good | 6747P | 48C/330W | Socket-compatible but NOT on OEM qualified list | [I]
C880A M8 | Row 72 | Training | Good | 6732P | 32C/350W | Socket-compatible but NOT on OEM qualified list | [I]
C880A M8 | Row 73 | Training | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
C880A M8 | Row 74 | Training | Better | 6767P | 64C/350W | Socket-compatible but NOT on OEM qualified list | [I]
C880A M8 | Row 75 | Training | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
C880A M8 | Row 76 | Training | Best | 6776P* | 64C/350W | Qualified by OEM | [I]
C880A M8 | Row 77 | Inference | Good | 6747P | 48C/330W | Socket-compatible but NOT on OEM qualified list | [I]
C880A M8 | Row 78 | Inference | Good | 6732P | 32C/350W | Socket-compatible but NOT on OEM qualified list | [I]
C880A M8 | Row 79 | Inference | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
C880A M8 | Row 80 | Inference | Better | 6767P | 64C/350W | Socket-compatible but NOT on OEM qualified list | [I]
C880A M8 | Row 81 | Inference | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
C880A M8 | Row 82 | Inference | Best | 6776P* | 64C/350W | Qualified by OEM | [I]

## Open_Questions
Risks and open questions
Items that change a planning number when resolved. Re-verify before any bid.
# | Open item | Why it matters | Resolve by
1 | Height 10RU (Cisco) vs 8U (catalog) | Rack density | Cisco spec sheet dimensions table
2 | PSU redundancy and 'System Power Consumption' row (truncated in retrieved excerpt) | Cisco publishes a system power figure - replace the estimate | Cisco C880A M8 spec sheet Table 1
3 | Per-DIMM, per-drive, per-NIC and fan power are planning assumptions [U] | Non-GPU load is 15-30% of node power | OEM power calculators: HPE Power Advisor, Dell EIPT, Lenovo Capacity Planner, Supermicro/MSI sales tools
4 | Workbook CPU SKUs 6960P / 6962P (rows 73, 75, 79, 81) are LGA-7529 | Not installable in LGA-4710 GPU chassis - only 6900P platforms (SYS-522GA-NRT, XE9780LAP) | Adopt socket as first filter in capacity planner

## Sources
Sources
Every [I]/[3P] row in this workbook cites one of these IDs. Internal companion files are marked Internal.
ID | Source | Location | Class
C1 | Cisco - UCS C880A M8 Rack Server Spec Sheet | https://www.cisco.com/c/dam/en/us/products/collateral/servers-unified-computing/ucs-c-series-rack-servers/ucs-c880a-m8-rack-server-spec-sheet.pdf | [I]
C2 | Cisco - UCS C880A M8 Data Sheet | https://www.cisco.com/c/en/us/products/collateral/servers-unified-computing/ucs-c-series-rack-servers/ucs-c880a-m8-rack-server-ds.html | [I]
C3 | NetBox Labs NDX - UCSC-C880A-M8 catalog entry (8U, 130 kg) | https://netboxlabs.com/ndx/cisco/cisco-ucsc-c880a-m8/ | [3P]
X5 | Internal - Intel_Xeon6_Workload_SKU_Recommendations.xlsx, sheet 'SKU Recommendations' rows 71-86 | Intel_Xeon6_Workload_SKU_Recommendations.xlsx | [I]

## Planner_YAML
Capacity-planner parameters (YAML)
Machine-readable block for Agentic Systems Capacity Planner ingestion. One line per row; copy column A verbatim.
system_option:
file: Cisco_B300.xlsx
oem: Cisco
gpu: B300
tier: "High-end"
chassis:
- model: "C880A M8"
rack_units: 10
cpu_socket: "LGA-4710"
power_scenarios: # inputs only; outputs live in 4_Power_Budget
- name: "B303 bundle · 12× 3200 W 54 V (6+6 assumed)"
system: "C880A M8"
gpus: 8
gpu_w: 1100
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 12, redundant: 6}
assumptions_u: {dimm_w: 10, drive_w: 20, nic_w: 25, baseboard_w: 1000, fan_pct: 0.1, psu_eff: 0.95}
- name: "B303 bundle · 12× 3200 W (10+2 assumed)"
system: "C880A M8"
gpus: 8
gpu_w: 1100
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 12, redundant: 2}
assumptions_u: {dimm_w: 10, drive_w: 20, nic_w: 25, baseboard_w: 1000, fan_pct: 0.1, psu_eff: 0.95}
compiled: "25 September 2026"