## Cover
Dell × NVIDIA H200 NVL — System Reference
OEM system options for the Mid-range (HBM/NVLink) tier · Xeon 6-hosted designs · Compiled 25 September 2026
Attribute | Value | Tag | Source
GPU | NVIDIA H200 NVL | [I]
Tier | Mid-range (HBM/NVLink) | [D]
System(s) | XE7740 | [I]
Host socket / series | XE7740: LGA-4710 (Xeon 6 (6700P; 'up to 144 cores' implies 6700E)) | [D]
GPU silicon reference | NVIDIA_H200-NVL_Reference.xlsx | [D]
Host CPU reference | Intel_Xeon6_Workload_SKU_Recommendations.xlsx rows 71-82 (see 5_Host_CPU_Map) | [I] | X5
Cross-OEM comparison | NVIDIA_Enterprise_GPU_Index.xlsx | [D]
POSITIONING
Dell's Xeon-hosted H200 NVL platform: 8× 600 W double-wide with NVLink bridges (Technical Guide).
Power at a glance (live links to 4_Power_Budget)
Scenario | Est. max DC load (W) | PSU redundant output (W) | Status
4× H200 NVL · 4× 3200 W (2+2) | 3862.08 | 6400 | OK within redundant capacity
8× H200 NVL · 8× 3200 W (4+4) @220-240 VAC | 6896.88 | 12800 | OK within redundant capacity
8× H200 NVL · 2900 W derate @200-220 VAC (4+4) | 6896.88 | 11600 | OK within redundant capacity
Provenance discipline
Tag | Meaning | Confidence | Use in planning
[I] | Vendor-published (NVIDIA datasheet/product page, OEM spec sheet, QuickSpecs, product guide) | High | Plan against
[D] | Derived here by stated arithmetic from [I] values (formula visible in cell) | Medium-High | Use; check formula
[3P] | Third-party measurement, reseller listing or press arithmetic | Medium | Cross-check before bid
[U] | Unpublished / unverified / planning assumption (editable input) | Low | Replace with OEM calculator output
[N] | Not applicable / not supported | - | -

## 1_System_Spec
1 · System specifications
One block per chassis. Conflicts between sources are shown side-by-side, not resolved silently.
XE7740 (Dell)
System | Section | Parameter | Value | Tag | Src
XE7740 | Identity | Model | Dell PowerEdge XE7740 | [I] | D1
XE7740 | Identity | Form factor | 4U, air-cooled | [I] | D1
XE7740 | Processor | CPU | Two Intel Xeon 6 series, up to 144 cores per processor (spec sheet) · up to 86 cores (support page) | [I] | D1, D3
XE7740 | Memory | Slots / max | 32 DDR5 RDIMM, max 8 TB (spec sheet) · 3 TB (reseller listings) | [I] | D1, D6
XE7740 | GPU | Slots | 8× PCIe Gen5 x16 DW-FHFL up to 600 W, or 16× PCIe Gen5 x16 SW-FHFL up to 75 W | [I] | D1
XE7740 | GPU | Supported NVIDIA GPUs | RTX PRO 6000 BSE 600 W (DW, 96 GB) · H200 NVL 600 W (DW, 141 GB) · H100 NVL 400 W · L40S 350 W · L4 72 W (SW) · RTX PRO 4500 165 W (SW, 32 GB); also Intel Gaudi 3 600 W | [I] | D1
XE7740 | GPU | NVLink | NVIDIA NVLink bridge section in Technical Guide | [I] | D4
XE7740 | Expansion | Network slots | Up to 8 PCIe Gen5 x16 SW-FHHL, each up to 150 W (front-serviceable backend NICs); 1× OCP 3.0 (x8) | [I] | D1
XE7740 | Storage | Drives | 8× 2.5" NVMe/SAS/SATA (122.88 TB) per spec sheet · 8× E3.S Gen5 per reseller listings | [I] | D1, D6
XE7740 | Storage | Boot | BOSS-N1: HWRAID 1, 2× M.2 NVMe | [I] | D1
XE7740 | Power | PSU options | 3200 W Titanium 200-240 VAC / 240 VDC (3200 W at 220.1-240 VAC; 2900 W at 200-220 VAC) · 3200 W Titanium 277 VAC / 336 VDC · 2400 W Titanium 200-240 VAC / 240 VDC | [I] | D1
XE7740 | Power | PSU count | 8 redundant AC or DC PSUs | [I] | D3
XE7740 | Power | PSU-GPU configuration matrix | Published in Technical Guide ch.10 (not retrieved) | [U] | D4
XE7740 | Cooling | Fans | 4 sets HPR in mid tray + 12 HPR on the front | [I] | D1
XE7740 | Physical | Dimensions | 174.3 mm H × 482 mm W × 899.56 mm D with bezel (886.73 mm without) | [I] | D1
XE7740 | Physical | Max weight | 71.35 kg | [I] | D1
XE7740 | Management | BMC / tools | iDRAC10, OME, OME Power Manager, RACADM, Redfish | [I] | D1
XE7740 | Security | Features | TPM 2.0, signed firmware, Silicon RoT, System Lockdown, SCV, chassis intrusion | [I] | D1
XE7740 | Ports | Front / rear | Front: USB-C iDRAC Direct, optional USB-A and mDP · Rear: iDRAC RJ45, 2× USB 3.1, VGA | [I] | D1
XE7740 | OS | Supported | Ubuntu Server LTS, RHEL, SLES, VMware ESXi | [I] | D1
XE7740 | This workbook | GPU population | NVIDIA H200 NVL — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]

## 2_Components
2 · Component and option list
Part / feature codes as published. Max qty is per system. Use for BOM drafting; confirm in OEM configurator.
System | Subsystem | Component | Part / feature code | Max qty | Spec | Tag | Src | Note
XE7740 | Processor | Intel Xeon 6 (P-core or E-core) | CTO | 2 | Up to 144C (E) / 86C (P) | [I] | D1, D3
XE7740 | Memory | DDR5 RDIMM | CTO | 32 |  | [I] | D1
XE7740 | Power | 3200 W Titanium 200-240 VAC / 240 VDC | CTO | 8 | 2900 W at 200-220 VAC | [I] | D1
XE7740 | Power | 3200 W Titanium 277 VAC / 336 VDC | CTO | 8 |  | [I] | D1
XE7740 | Power | 2400 W Titanium 200-240 VAC / 240 VDC | CTO | 8 |  | [I] | D1
XE7740 | Boot | BOSS-N1 | CTO | 1 | 2× M.2 NVMe HWRAID1 | [I] | D1
XE7740 | Network | OCP NIC 3.0 | CTO | 1 | x8 lanes | [I] | D1
XE7740 | Network | Backend PCIe NIC slots | CTO | 8 | Gen5 x16 FHHL ≤150 W | [I] | D1

## 3_Power_Rules
3 · OEM-published power and PSU rules
These constrain the scenarios on 4_Power_Budget. [U] rows are gaps to close with the OEM.
System | Rule | Tag | Src
XE7740 | 3200 W 200-240 VAC PSU delivers 3200 W only at 220.1-240 VAC; derates to 2900 W at 200-220 VAC | [I] | D1
XE7740 | Alternative PSUs: 3200 W 277 VAC / 336 VDC; 2400 W 200-240 VAC | [I] | D1
XE7740 | Up to 8 redundant AC or DC PSUs | [I] | D3
XE7740 | Double-wide GPU slots ≤600 W each (8); single-wide ≤75 W each (16); backend NIC slots ≤150 W each (8) | [I] | D1
XE7740 | PSU-to-GPU configuration matrix exists in Technical Guide ch.10 - not retrieved; required quantities unknown here | [U] | D4

## 4_Power_Budget
4 · Node power budget and rack fit (live model)
Blue-on-yellow cells are inputs. Component load is compared with PSU OUTPUT capacity in redundant mode; AC input and rack fit use PSU efficiency. Replace [U] inputs with OEM calculator output before any facility commitment.
Input | Unit | 4× H200 NVL · 4× 3200 W (2+2) | 8× H200 NVL · 8× 3200 W (4+4) @220-240 VAC | 8× H200 NVL · 2900 W derate @200-220 VAC (4+4) | Tag | Basis
System |  | XE7740 | XE7740 | XE7740
GPUs installed | count | 4 | 8 | 8 | [I] | OEM max / scenario choice
GPU max power | W | 600 | 600 | 600 | [I] | NVIDIA / OEM GPU TDP
CPUs | count | 2 | 2 | 2 | [I] | OEM spec
CPU TDP | W | 350 | 350 | 350 | [U] | Scenario SKU choice - see 5_Host_CPU_Map
DIMMs | count | 16 | 32 | 32 | [U] | Scenario choice (max per 1_System_Spec)
Power per DDR5 RDIMM | W | 10 | 10 | 10 | [U] | Planning assumption; replace with OEM calculator
Data drives (NVMe) | count | 4 | 8 | 8 | [U] | Scenario choice
Power per data drive | W | 25 | 25 | 25 | [U] | Planning assumption: Gen5 U.2/E3.S ≈25 W, E1.S ≈20 W
Boot drives (M.2) | count | 2 | 2 | 2 | [I] | OEM spec
Power per boot drive | W | 8 | 8 | 8 | [U] | Planning assumption
Add-in NICs / DPUs | count | 2 | 4 | 4 | [U] | Scenario choice (N-S and/or E-W add-in)
Power per NIC / DPU | W | 25 | 25 | 25 | [U] | Planning assumption: CX-7 class ≈25 W; BlueField-3 ≈75 W
Baseboard / PCIe switch / NVSwitch / on-board CX-8 overhead | W | 150 | 250 | 250 | [U] | Planning placeholder - largest uncertainty on HGX nodes
Fans, VRs and conversion overhead | % of component load | 8% | 8% | 8% | [U] | Planning assumption
PSU efficiency at operating load | fraction | 0.95 | 0.95 | 0.95 | [U] | 80 PLUS Titanium ≈94-96% (HPE states up to 96%)
PSU output rating at site input voltage (0 = unpublished) | W | 3200 | 3200 | 2900 | [I] | OEM spec
PSUs installed | count | 4 | 8 | 8 | [I] / [U] | OEM spec / scenario
PSUs held for redundancy | count | 2 | 4 | 4 | [U] | N+1 = 1, N+N = half
PSUs in dedicated GPU power domain (0 = not modelled) | count | 0 | 0 | 0 | [I] | HPE DL380a only
Rack power budget | kW | 30 | 30 | 30 | [U] | Your facility figure
Node height | RU | 4 | 4 | 4 | [I] | OEM spec
Usable rack units for compute | RU | 38 | 38 | 38 | [U] | 42U minus ToR, PDU, patch
Outputs (formulas)
Output | Unit | 4× H200 NVL · 4× 3200 W (2+2) | 8× H200 NVL · 8× 3200 W (4+4) @220-240 VAC | 8× H200 NVL · 2900 W derate @200-220 VAC (4+4) | Tag | Formula basis
GPU load | W | 2400 | 4800 | 4800 | [D] | GPUs × GPU W
CPU load | W | 700 | 700 | 700 | [D] | CPUs × TDP
Memory load | W | 160 | 320 | 320 | [D] | DIMMs × W
Storage load | W | 116 | 216 | 216 | [D] | drives × W + boot × W
Network add-in load | W | 50 | 100 | 100 | [D] | NICs × W
Baseboard / switch overhead | W | 150 | 250 | 250 | [D] | input
Component subtotal | W | 3576 | 6386 | 6386 | [D] | sum of above
Fans / VR / conversion | W | 286.08 | 510.88 | 510.88 | [D] | subtotal × %
Estimated max DC load | W | 3862.08 | 6896.88 | 6896.88 | [D] | subtotal + fans
GPU share of DC load | % | 62.14% | 69.6% | 69.6% | [D] | GPU ÷ DC
Estimated max AC input | W | 4065.3474 | 7259.8737 | 7259.8737 | [D] | DC ÷ efficiency
PSU output in redundant mode | W | 6400 | 12800 | 11600 | [D] | (installed − redundant) × rating
Headroom (redundant) | W | 2537.92 | 5903.12 | 4703.12 | [D] | capacity − DC load
PSU utilisation (redundant) | % | 60.35% | 53.88% | 59.46% | [D] | DC ÷ capacity
Redundancy check |  | OK within redundant capacity | OK within redundant capacity | OK within redundant capacity | [D]
GPU-domain PSU output (no domain redundancy) | W | n/a | n/a | n/a | [D] | GPU-domain PSUs × rating
GPU-domain check |  | n/a | n/a | n/a | [D] | GPU load ≤ domain output
Heat load | BTU/hr | 13870.9652 | 24770.689 | 24770.689 | [D] | AC W × 3.412
AC power per GPU (all-in) | kW | 1.0163 | 0.90748 | 0.90748 | [D] | AC ÷ GPUs
Nodes per rack - power limited | count | 7 | 4 | 4 | [D] | rack W ÷ node AC
Nodes per rack - space limited | count | 9 | 9 | 9 | [D] | usable RU ÷ node RU
Nodes per rack | count | 7 | 4 | 4 | [D] | min(power, space)
GPUs per rack | count | 28 | 32 | 32 | [D] | nodes × GPUs
Rack AC load at that fit | kW | 28.4574 | 29.0395 | 29.0395 | [D] | nodes × AC
Estimate is a planning ceiling at nameplate GPU/CPU power, not a measured draw. Sustained inference typically runs below nameplate; training and burn-in approach it. PSU ratings are OUTPUT watts at the stated input voltage - check derates (e.g., Dell 3200 W → 2900 W at 200-220 VAC; Lenovo 3200 W is 230 V-only).

## 5_Host_CPU_Map
5 · Host CPU map against the Xeon 6 SKU workbook
Rows 71-82 of 'SKU Recommendations' (GPU host CPU). Socket is the first filter; OEM qualified list the second.
XE7740 — socket LGA-4710; series Xeon 6 (6700P; 'up to 144 cores' implies 6700E)
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
XE7740 | Row 71 | Training | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 72 | Training | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 73 | Training | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
XE7740 | Row 74 | Training | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 75 | Training | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
XE7740 | Row 76 | Training | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 77 | Inference | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 78 | Inference | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 79 | Inference | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
XE7740 | Row 80 | Inference | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
XE7740 | Row 81 | Inference | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
XE7740 | Row 82 | Inference | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]

## Open_Questions
Risks and open questions
Items that change a planning number when resolved. Re-verify before any bid.
# | Open item | Why it matters | Resolve by
1 | XE7740 PSU-GPU configuration matrix (Tech Guide ch.10) | Required PSU count and redundancy per GPU population | Dell XE7740 Technical Guide E118S
2 | Per-DIMM, per-drive, per-NIC and fan power are planning assumptions [U] | Non-GPU load is 15-30% of node power | OEM power calculators: HPE Power Advisor, Dell EIPT, Lenovo Capacity Planner, Supermicro/MSI sales tools
3 | Workbook CPU SKUs 6960P / 6962P (rows 73, 75, 79, 81) are LGA-7529 | Not installable in LGA-4710 GPU chassis - only 6900P platforms (SYS-522GA-NRT, XE9780LAP) | Adopt socket as first filter in capacity planner

## Sources
Sources
Every [I]/[3P] row in this workbook cites one of these IDs. Internal companion files are marked Internal.
ID | Source | Location | Class
D1 | Dell - PowerEdge XE series AI spec sheet (Rev A07) | https://www.delltechnologies.com/asset/en-us/products/servers/technical-support/poweredge-xe-ai-spec-sheet.pdf | [I]
D3 | Dell - PowerEdge XE7740 support overview | https://www.dell.com/support/product-details/en-us/product/poweredge-xe7740/overview | [I]
D4 | Dell - PowerEdge XE7740 Technical Guide E118S Rev A04 (Apr 2026) - PSU-GPU matrix not retrieved | https://www.delltechnologies.com/asset/en-nz/products/servers/technical-support/poweredge-xe7740-technical-guide.pdf | [I]
D6 | ServerMonkey / Network Devices - XE7740 listings | https://www.servermonkey.com/servers/ai-ml-servers/dell-emc-gpu-servers/dell-poweredge-xe7740.html | [3P]
X5 | Internal - Intel_Xeon6_Workload_SKU_Recommendations.xlsx, sheet 'SKU Recommendations' rows 71-86 | Intel_Xeon6_Workload_SKU_Recommendations.xlsx | [I]

## Planner_YAML
Capacity-planner parameters (YAML)
Machine-readable block for Agentic Systems Capacity Planner ingestion. One line per row; copy column A verbatim.
system_option:
file: Dell_H200-NVL.xlsx
oem: Dell
gpu: H200-NVL
tier: "Mid-range (HBM/NVLink)"
chassis:
- model: "XE7740"
rack_units: 4
cpu_socket: "LGA-4710"
power_scenarios: # inputs only; outputs live in 4_Power_Budget
- name: "4× H200 NVL · 4× 3200 W (2+2)"
system: "XE7740"
gpus: 4
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 4, redundant: 2}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 150, fan_pct: 0.08, psu_eff: 0.95}
- name: "8× H200 NVL · 8× 3200 W (4+4) @220-240 VAC"
system: "XE7740"
gpus: 8
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 8, redundant: 4}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 250, fan_pct: 0.08, psu_eff: 0.95}
- name: "8× H200 NVL · 2900 W derate @200-220 VAC (4+4)"
system: "XE7740"
gpus: 8
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 2900, installed: 8, redundant: 4}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 250, fan_pct: 0.08, psu_eff: 0.95}
compiled: "25 September 2026"