## Cover
HPE × NVIDIA H200 NVL — System Reference
OEM system options for the Mid-range (HBM/NVLink) tier · Xeon 6-hosted designs · Compiled 25 September 2026
Attribute | Value | Tag | Source
GPU | NVIDIA H200 NVL | [I]
Tier | Mid-range (HBM/NVLink) | [D]
System(s) | DL380a Gen12 | [I]
Host socket / series | DL380a Gen12: LGA-4710 (Xeon 6700P / 6700E (6500P)) | [D]
GPU silicon reference | NVIDIA_H200-NVL_Reference.xlsx | [D]
Host CPU reference | Intel_Xeon6_Workload_SKU_Recommendations.xlsx rows 71-82 (see 5_Host_CPU_Map) | [I] | X5
Cross-OEM comparison | NVIDIA_Enterprise_GPU_Index.xlsx | [D]
POSITIONING
The only HPE mainstream chassis that takes 10 double-wide H200 NVL and the 4-way NVLink bridge; the HBM/NVLink mid-tier option with 5-year NVAIE bundled.
Power at a glance (live links to 4_Power_Budget)
Scenario | Est. max DC load (W) | PSU redundant output (W) | Status
4× H200 NVL (one 4-way NVLink island) · 5× 3200 W | 3862.08 | 12800 | OK within redundant capacity
8× H200 NVL (two 4-way islands) · 8× 3200 W | 6896.88 | 22400 | OK within redundant capacity
10× H200 NVL (max) · 8× 3200 W | 8138.88 | 22400 | OK within redundant capacity
Provenance discipline
Tag | Meaning | Confidence | Use in planning
[I] | Vendor-published (NVIDIA datasheet/product page, OEM spec sheet, QuickSpecs, product guide) | High | Plan against
[D] | Derived here by stated arithmetic from [I] values (formula visible in cell) | Medium-High | Use; check formula
[3P] | Third-party measurement, reseller listing or press arithmetic | Medium | Cross-check before bid
[U] | Unpublished / unverified / planning assumption (editable input) | Low | Replace with OEM calculator output
[N] | Not applicable / not supported | - | -

## 1_System_Spec
1 · System specifications
One block per chassis. Conflicts between sources are shown side-by-side, not resolved silently.
DL380a Gen12 (HPE)
System | Section | Parameter | Value | Tag | Src
DL380a Gen12 | Identity | Model | HPE ProLiant Compute DL380a Gen12 | [I] | H2
DL380a Gen12 | Identity | CTO base SKUs | P74461-B21 (8DW, iLO 6 - not upgradable to iLO 7); P76706-B21 (8DW/16SW) | [I] | H1, H5
DL380a Gen12 | Identity | Form factor | 4U, 2-socket rack | [I] | H2
DL380a Gen12 | Processor | CPU | Up to 2× Intel Xeon 6; up to 144 cores at 250 W (E-core 6700E) - P-core 6700P options also offered | [I] | H2
DL380a Gen12 | Processor | Socket | LGA-4710 (6700/6500 platform) | [D]
DL380a Gen12 | Memory | Slots / speed | 32 DDR5 DIMMs, up to 6400 MT/s | [I] | H1
DL380a Gen12 | Memory | Max capacity | Up to 4 TB (HPE store) · 8 TB (reseller part list) | [I] | H1, H5
DL380a Gen12 | GPU | Supported configurations | Up to 16 single-wide NVIDIA L4, or 10 double-wide L40S / H100 NVL / H200 NVL, or 8 double-wide RTX PRO 6000 BSE | [I] | H2
DL380a Gen12 | GPU | Per-GPU power | Double-wide GPUs up to 600 W each | [3P] | H5
DL380a Gen12 | GPU | GPU interconnect | NVIDIA 4-way NVLink bridge between neighbouring GPUs (H100/H200 NVL); PCIe Gen5 switch boards and captive risers | [I] | H1, H5
DL380a Gen12 | Expansion | Slots | Up to 6× PCIe Gen5 x16 + 2× OCP 3.0 (rear) | [I] | H1
DL380a Gen12 | Storage | Front bays | 8× SFF NVMe or 16× EDSFF E3.S; plus 2× NVMe boot (NS204i-u v2) | [I] | H1, H5
DL380a Gen12 | Power | PSU family | HPE M-CRPS Titanium hot-plug: 1500 W / 2400 W / 3200 W; up to 96% efficiency | [I] | H1
DL380a Gen12 | Power | PSU count | Up to 8 PSUs | [I] | H1, H3
DL380a Gen12 | Power | Power domains | Three power domains - two with six PSUs dedicated to GPUs | [I] | H2
DL380a Gen12 | Power | Heat (2400 W PSU) | 8,572 BTU/hr @200 VAC · 8,540 @220 VAC · 8,539 @240 VAC | [I] | H1
DL380a Gen12 | Power | Heat (3200 W PSU) | 10,577 BTU/hr @200 VAC · 11,713 @220 VAC · 11,699 @240 VAC | [I] | H1
DL380a Gen12 | Cooling | Method | Air-cooled; optional Direct Liquid Cooling (DLC) | [I] | H2
DL380a Gen12 | Cooling | Fans | 4 hot-plug fan assemblies | [3P] | H5
DL380a Gen12 | Environment | Inlet temperature | 10-35 °C at sea level; derate 1.0 °C per 305 m to 3,050 m; extended 5-40 °C for approved configurations; performance may reduce above 30 °C with a fan fault | [I] | H1
DL380a Gen12 | Management | BMC | HPE iLO 7 (iLO 6 on P74461-B21); Silicon Root of Trust; detachable DC-MHS iLO module | [I] | H1, H3
DL380a Gen12 | Physical | Dimensions / weight | Not captured in retrieved sources | [U]
DL380a Gen12 | This workbook | GPU population | NVIDIA H200 NVL — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]

## 2_Components
2 · Component and option list
Part / feature codes as published. Max qty is per system. Use for BOM drafting; confirm in OEM configurator.
System | Subsystem | Component | Part / feature code | Max qty | Spec | Tag | Src | Note
DL380a Gen12 | Processor | Intel Xeon 6 (6700P P-core or 6700E E-core) | CTO | 2 | E-core parts: no AMX | [I] | H2 | Pick P-core for host-side AMX inference
DL380a Gen12 | Memory | DDR5 RDIMM | CTO | 32 | Up to 6400 MT/s | [I] | H1
DL380a Gen12 | GPU | NVIDIA RTX PRO 6000 Blackwell 96GB PCIe | S6A73C | 8 | 600 W DW | [3P] | H5
DL380a Gen12 | GPU | NVIDIA RTX PRO 6000D Blackwell 48GB PCIe | S6W21C | 8 | Regional variant | [3P] | H5
DL380a Gen12 | GPU | NVIDIA H200 NVL 141GB PCIe | S3U30C | 10 | 600 W DW | [3P] | H5
DL380a Gen12 | GPU | NVIDIA 2-way NVLink Bridge for H200 NVL | S4A90C | - |  | [3P] | H5
DL380a Gen12 | GPU | NVIDIA 4-way NVLink Bridge for H200 NVL | S4A91C | - | 900 GB/s | [3P] | H5
DL380a Gen12 | GPU | HPE NVIDIA L4 SW 24GB 72W | S0K89C | 16 | 72 W SW | [3P] | H5
DL380a Gen12 | GPU | HPE NVIDIA L40S DW 48GB 300W | S2L70C | 10 |  | [3P] | H5
DL380a Gen12 | GPU | HPE NVIDIA L20 48GB 300W | S4A92C | - |  | [3P] | H5
DL380a Gen12 | Power | HPE M-CRPS 1500W Titanium Hot Plug PSU Kit | P67244-B21 | 8 | Ships with C13-C14 2 m cord P67847-B21 | [3P] | H3, H1
DL380a Gen12 | Power | HPE M-CRPS 2400W Titanium Hot Plug PSU Kit | P67252-B21 | 8 | C19 only; ships with C19-C20 2 m cord P67845-B21 | [3P] | H3, H1
DL380a Gen12 | Power | HPE M-CRPS 3200W Titanium Hot Plug PSU Kit | P67248-B21 | 8 | C19 only | [3P] | H3
DL380a Gen12 | Power | PDB kit | (QuickSpecs) | 1 | Required on P74461-B21 when >5 PSUs | [I] | H1
DL380a Gen12 | Boot | HPE NS204i-u v2 Boot Optimized Storage Device |  | 1 | 2× NVMe M.2 RAID1 | [3P] | H5
DL380a Gen12 | Management | HPE iLO 7 | embedded | 1 |  | [I] | H1

## 3_Power_Rules
3 · OEM-published power and PSU rules
These constrain the scenarios on 4_Power_Budget. [U] rows are gaps to close with the OEM.
System | Rule | Tag | Src
DL380a Gen12 | 2400 W or 3200 W PSUs are required for H100 / H200 NVL GPUs | [I] | H1
DL380a Gen12 | Quantity 5 PSUs (2 for system board, 3 for GPUs) required for 2 or 4 double-wide GPU configurations | [I] | H1
DL380a Gen12 | Quantity 8 PSUs required for 8 or 10 double-wide GPU configurations | [I] | H1
DL380a Gen12 | P74461-B21 (8DW CTO): more than 5 PSUs requires 1× PDB kit; P76706-B21 (8DW/16SW) needs no PDB | [I] | H1
DL380a Gen12 | 2400 W and 3200 W PSUs support C19 / C19-C20 cords only; cord count must match PSU count on P76706-B21 | [I] | H1
DL380a Gen12 | Three power domains; two domains of six PSUs dedicated to GPUs | [I] | H2
DL380a Gen12 | Run HPE Power Advisor before PSU selection | [I] | H1
DL380a Gen12 | Reviewed unit: 4× RTX PRO 6000 (600 W) on five 2400 W PSUs, N+1 | [3P] | H3

## 4_Power_Budget
4 · Node power budget and rack fit (live model)
Blue-on-yellow cells are inputs. Component load is compared with PSU OUTPUT capacity in redundant mode; AC input and rack fit use PSU efficiency. Replace [U] inputs with OEM calculator output before any facility commitment.
Input | Unit | 4× H200 NVL (one 4-way NVLink island) · 5× 3200 W | 8× H200 NVL (two 4-way islands) · 8× 3200 W | 10× H200 NVL (max) · 8× 3200 W | Tag | Basis
System |  | DL380a Gen12 | DL380a Gen12 | DL380a Gen12
GPUs installed | count | 4 | 8 | 10 | [I] | OEM max / scenario choice
GPU max power | W | 600 | 600 | 600 | [I] | NVIDIA / OEM GPU TDP
CPUs | count | 2 | 2 | 2 | [I] | OEM spec
CPU TDP | W | 350 | 350 | 350 | [U] | Scenario SKU choice - see 5_Host_CPU_Map
DIMMs | count | 16 | 32 | 32 | [U] | Scenario choice (max per 1_System_Spec)
Power per DDR5 RDIMM | W | 10 | 10 | 10 | [U] | Planning assumption; replace with OEM calculator
Data drives (NVMe) | count | 4 | 8 | 8 | [U] | Scenario choice
Power per data drive | W | 25 | 25 | 25 | [U] | Planning assumption: Gen5 U.2/E3.S ≈25 W, E1.S ≈20 W
Boot drives (M.2) | count | 2 | 2 | 2 | [I] | OEM spec
Power per boot drive | W | 8 | 8 | 8 | [U] | Planning assumption
Add-in NICs / DPUs | count | 2 | 4 | 2 | [U] | Scenario choice (N-S and/or E-W add-in)
Power per NIC / DPU | W | 25 | 25 | 25 | [U] | Planning assumption: CX-7 class ≈25 W; BlueField-3 ≈75 W
Baseboard / PCIe switch / NVSwitch / on-board CX-8 overhead | W | 150 | 250 | 250 | [U] | Planning placeholder - largest uncertainty on HGX nodes
Fans, VRs and conversion overhead | % of component load | 8% | 8% | 8% | [U] | Planning assumption
PSU efficiency at operating load | fraction | 0.95 | 0.95 | 0.95 | [U] | 80 PLUS Titanium ≈94-96% (HPE states up to 96%)
PSU output rating at site input voltage (0 = unpublished) | W | 3200 | 3200 | 3200 | [I] | OEM spec
PSUs installed | count | 5 | 8 | 8 | [I] | OEM spec / scenario
PSUs held for redundancy | count | 1 | 1 | 1 | [U] | N+1 = 1, N+N = half
PSUs in dedicated GPU power domain (0 = not modelled) | count | 3 | 6 | 6 | [I] | HPE DL380a only
Rack power budget | kW | 30 | 30 | 30 | [U] | Your facility figure
Node height | RU | 4 | 4 | 4 | [I] | OEM spec
Usable rack units for compute | RU | 38 | 38 | 38 | [U] | 42U minus ToR, PDU, patch
Outputs (formulas)
Output | Unit | 4× H200 NVL (one 4-way NVLink island) · 5× 3200 W | 8× H200 NVL (two 4-way islands) · 8× 3200 W | 10× H200 NVL (max) · 8× 3200 W | Tag | Formula basis
GPU load | W | 2400 | 4800 | 6000 | [D] | GPUs × GPU W
CPU load | W | 700 | 700 | 700 | [D] | CPUs × TDP
Memory load | W | 160 | 320 | 320 | [D] | DIMMs × W
Storage load | W | 116 | 216 | 216 | [D] | drives × W + boot × W
Network add-in load | W | 50 | 100 | 50 | [D] | NICs × W
Baseboard / switch overhead | W | 150 | 250 | 250 | [D] | input
Component subtotal | W | 3576 | 6386 | 7536 | [D] | sum of above
Fans / VR / conversion | W | 286.08 | 510.88 | 602.88 | [D] | subtotal × %
Estimated max DC load | W | 3862.08 | 6896.88 | 8138.88 | [D] | subtotal + fans
GPU share of DC load | % | 62.14% | 69.6% | 73.72% | [D] | GPU ÷ DC
Estimated max AC input | W | 4065.3474 | 7259.8737 | 8567.2421 | [D] | DC ÷ efficiency
PSU output in redundant mode | W | 12800 | 22400 | 22400 | [D] | (installed − redundant) × rating
Headroom (redundant) | W | 8937.92 | 15503.12 | 14261.12 | [D] | capacity − DC load
PSU utilisation (redundant) | % | 30.17% | 30.79% | 36.33% | [D] | DC ÷ capacity
Redundancy check |  | OK within redundant capacity | OK within redundant capacity | OK within redundant capacity | [D]
GPU-domain PSU output (no domain redundancy) | W | 9600 | 19200 | 19200 | [D] | GPU-domain PSUs × rating
GPU-domain check |  | OK | OK | OK | [D] | GPU load ≤ domain output
Heat load | BTU/hr | 13870.9652 | 24770.689 | 29231.4301 | [D] | AC W × 3.412
AC power per GPU (all-in) | kW | 1.0163 | 0.90748 | 0.85672 | [D] | AC ÷ GPUs
Nodes per rack - power limited | count | 7 | 4 | 3 | [D] | rack W ÷ node AC
Nodes per rack - space limited | count | 9 | 9 | 9 | [D] | usable RU ÷ node RU
Nodes per rack | count | 7 | 4 | 3 | [D] | min(power, space)
GPUs per rack | count | 28 | 32 | 30 | [D] | nodes × GPUs
Rack AC load at that fit | kW | 28.4574 | 29.0395 | 25.7017 | [D] | nodes × AC
Estimate is a planning ceiling at nameplate GPU/CPU power, not a measured draw. Sustained inference typically runs below nameplate; training and burn-in approach it. PSU ratings are OUTPUT watts at the stated input voltage - check derates (e.g., Dell 3200 W → 2900 W at 200-220 VAC; Lenovo 3200 W is 230 V-only).

## 5_Host_CPU_Map
5 · Host CPU map against the Xeon 6 SKU workbook
Rows 71-82 of 'SKU Recommendations' (GPU host CPU). Socket is the first filter; OEM qualified list the second.
DL380a Gen12 — socket LGA-4710; series Xeon 6700P / 6700E (6500P)
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
DL380a Gen12 | Row 71 | Training | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 72 | Training | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 73 | Training | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
DL380a Gen12 | Row 74 | Training | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 75 | Training | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
DL380a Gen12 | Row 76 | Training | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 77 | Inference | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 78 | Inference | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 79 | Inference | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
DL380a Gen12 | Row 80 | Inference | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
DL380a Gen12 | Row 81 | Inference | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
DL380a Gen12 | Row 82 | Inference | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]

## Open_Questions
Risks and open questions
Items that change a planning number when resolved. Re-verify before any bid.
# | Open item | Why it matters | Resolve by
1 | NVLink island layout for 10 GPUs (two 4-way + one 2-way?) | TP placement | HPE QuickSpecs GPU section
2 | Per-DIMM, per-drive, per-NIC and fan power are planning assumptions [U] | Non-GPU load is 15-30% of node power | OEM power calculators: HPE Power Advisor, Dell EIPT, Lenovo Capacity Planner, Supermicro/MSI sales tools
3 | Workbook CPU SKUs 6960P / 6962P (rows 73, 75, 79, 81) are LGA-7529 | Not installable in LGA-4710 GPU chassis - only 6900P platforms (SYS-522GA-NRT, XE9780LAP) | Adopt socket as first filter in capacity planner

## Sources
Sources
Every [I]/[3P] row in this workbook cites one of these IDs. Internal companion files are marked Internal.
ID | Source | Location | Class
H1 | HPE - ProLiant Compute DL380a Gen12 QuickSpecs (a00047453enw) | https://www.hpe.com/psnow/doc/a00047453enw | [I]
H2 | HPE - ProLiant Compute DL380a Gen12 product page | https://www.hpe.com/us/en/compute/hpe-proliant-compute/dl380a-gen12.html | [I]
H3 | StorageReview - HPE DL380a Gen12 review (24 Nov 2025) | https://www.storagereview.com/review/hpe-proliant-dl380a-gen12-review-air-cooled-4u-server-for-dense-multi-gpu-ai | [3P]
H5 | Express Computer Systems - DL380a Gen12 configurable part list | https://expresscomputersystems.com/products/hpe-proliant-dl380a-rack-server-gen-12-configurable | [3P]
X5 | Internal - Intel_Xeon6_Workload_SKU_Recommendations.xlsx, sheet 'SKU Recommendations' rows 71-86 | Intel_Xeon6_Workload_SKU_Recommendations.xlsx | [I]

## Planner_YAML
Capacity-planner parameters (YAML)
Machine-readable block for Agentic Systems Capacity Planner ingestion. One line per row; copy column A verbatim.
system_option:
file: HPE_H200-NVL.xlsx
oem: HPE
gpu: H200-NVL
tier: "Mid-range (HBM/NVLink)"
chassis:
- model: "DL380a Gen12"
rack_units: 4
cpu_socket: "LGA-4710"
power_scenarios: # inputs only; outputs live in 4_Power_Budget
- name: "4× H200 NVL (one 4-way NVLink island) · 5× 3200 W"
system: "DL380a Gen12"
gpus: 4
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 5, redundant: 1}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 150, fan_pct: 0.08, psu_eff: 0.95}
- name: "8× H200 NVL (two 4-way islands) · 8× 3200 W"
system: "DL380a Gen12"
gpus: 8
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 8, redundant: 1}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 250, fan_pct: 0.08, psu_eff: 0.95}
- name: "10× H200 NVL (max) · 8× 3200 W"
system: "DL380a Gen12"
gpus: 10
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 8, redundant: 1}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 250, fan_pct: 0.08, psu_eff: 0.95}
compiled: "25 September 2026"