## Cover
MSI × NVIDIA H200 NVL — System Reference
OEM system options for the Mid-range (HBM/NVLink) tier · Xeon 6-hosted designs · Compiled 25 September 2026
Attribute | Value | Tag | Source
GPU | NVIDIA H200 NVL | [I]
Tier | Mid-range (HBM/NVLink) | [D]
System(s) | CG480-S5063 · CG290-S3063 | [I]
Host socket / series | CG480-S5063: LGA-4710 (Socket E2) (Xeon 6700E / 6500P / 6700P) · CG290-S3063: (single Xeon 6 - socket unverified) (Xeon 6 (1S)) | [D]
GPU silicon reference | NVIDIA_H200-NVL_Reference.xlsx | [D]
Host CPU reference | Intel_Xeon6_Workload_SKU_Recommendations.xlsx rows 71-82 (see 5_Host_CPU_Map) | [I] | X5
Cross-OEM comparison | NVIDIA_Enterprise_GPU_Index.xlsx | [D]
POSITIONING
MSI's NVIDIA MGX RTX PRO Servers: CG480-S5063 (4U, 2× Xeon 6, 8 GPUs, 2-8-5-200) and CG290-S3063 (2U, 1× Xeon 6, 4 GPUs, 1-4-3). The CG480 has the most published detail on power and environment among the MGX builds.
Power at a glance (live links to 4_Power_Budget)
Scenario | Est. max DC load (W) | PSU redundant output (W) | Status
CG480 · 8× H200 NVL · 4× 3200 W (3+1) | 6863.4 | 9600 | OK within redundant capacity
CG290 · 4× H200 NVL · PSU unpublished | 3511.08 | n/a | PSU data not published
Provenance discipline
Tag | Meaning | Confidence | Use in planning
[I] | Vendor-published (NVIDIA datasheet/product page, OEM spec sheet, QuickSpecs, product guide) | High | Plan against
[D] | Derived here by stated arithmetic from [I] values (formula visible in cell) | Medium-High | Use; check formula
[3P] | Third-party measurement, reseller listing or press arithmetic | Medium | Cross-check before bid
[U] | Unpublished / unverified / planning assumption (editable input) | Low | Replace with OEM calculator output
[N] | Not applicable / not supported | - | -

## 1_System_Spec
1 · System specifications
One block per chassis. Conflicts between sources are shown side-by-side, not resolved silently.
CG480-S5063 (MSI)
System | Section | Parameter | Value | Tag | Src
CG480-S5063 | Identity | Model | MSI CG480-S5063 (S5063G480RAE20), board MS-S405; NVIDIA-Certified | [I] | M2, M5
CG480-S5063 | Identity | Form factor | 4U, NVIDIA MGX modular architecture | [I] | M1
CG480-S5063 | Processor | CPU | Dual Intel Xeon 6700E / 6500P / 6700P, TDP ≤350 W; 2 air-cooling modules | [I] | M1, M5
CG480-S5063 | Memory | Slots / speed | 32 DDR5 RDIMM/MRDIMM, 8 ch per CPU (2 DPC); 6400 MT/s 1 DPC, 5200 MT/s 2 DPC; up to 8 TB | [I] | M3, M5
CG480-S5063 | GPU | Capacity | Up to 8 double-wide PCIe GPUs ≤600 W: RTX PRO 6000 BSE or H200 NVL | [I] | M2, M5
CG480-S5063 | GPU | Topology | 2-8-5-200 CPU:GPU:NIC; PCIe switch board | [I] | M3, M5
CG480-S5063 | Expansion | Slots | Up to 13 PCIe 5.0 x16 | [I] | M2
CG480-S5063 | Storage | Bays | 20× hot-swap E1.S PCIe 5.0 x4 NVMe | [I] | M3, M5
CG480-S5063 | Network | LAN | 2× 10GBase-T (Intel X710-AT2, NCSI) + 1× 1GbE BMC | [I] | M2
CG480-S5063 | Power | PSUs | (3+1) redundant 3200 W CRPS, 80 PLUS Titanium | [I] | M1
CG480-S5063 | Cooling | Fans | 10× 8080 hot-swap (5 upper for GPU, 5 lower for CPU) | [I] | M1, M5
CG480-S5063 | Environment | Temperature | Operating 0-35 °C; non-operating -20 to 70 °C; 5-85% RH non-condensing | [I] | M1
CG480-S5063 | Management | BMC | ASPEED AST2600, IPMI 2.0, Redfish; dual BIOS & BMC; TPM 2.0; optional hardware RoT | [I] | M2
CG480-S5063 | Regulatory | Certs | FCC Class A, CE | [I] | M1
CG480-S5063 | This workbook | GPU population | NVIDIA H200 NVL — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]
CG290-S3063 (MSI)
System | Section | Parameter | Value | Tag | Src
CG290-S3063 | Identity | Model | MSI CG290-S3063 | [I] | M3
CG290-S3063 | Identity | Form factor | 2U, NVIDIA MGX | [I] | M3
CG290-S3063 | Processor | CPU | Single Intel Xeon 6 | [I] | M3
CG290-S3063 | Memory | Slots | Up to 16 DDR5 DIMM | [I] | M3
CG290-S3063 | GPU | Capacity | Four FHFL double-wide GPUs (RTX PRO 6000 BSE / H200 NVL); 1-4-3 topology; up to 8 PCIe 5.0 x16 slots | [I] | M3, M4
CG290-S3063 | Storage | Bays | 4× rear PCIe 5.0 U.2 NVMe + 2× M.2 | [I] | M3
CG290-S3063 | Power | PSUs | Not captured | [U]
CG290-S3063 | This workbook | GPU population | NVIDIA H200 NVL — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]

## 2_Components
2 · Component and option list
Part / feature codes as published. Max qty is per system. Use for BOM drafting; confirm in OEM configurator.
System | Subsystem | Component | Part / feature code | Max qty | Spec | Tag | Src | Note
CG480-S5063 | Power | 3200 W CRPS Titanium PSU |  | 4 | 3+1 | [I] | M1
CG480-S5063 | Cooling | 8080 hot-swap fan |  | 10 |  | [I] | M1
CG480-S5063 | Storage | E1.S PCIe 5.0 x4 NVMe bay |  | 20 |  | [I] | M5
CG480-S5063 | Board | PCIe switch board |  | 1 |  | [I] | M5

## 3_Power_Rules
3 · OEM-published power and PSU rules
These constrain the scenarios on 4_Power_Budget. [U] rows are gaps to close with the OEM.
System | Rule | Tag | Src
CG480-S5063 | (3+1) redundant 3200 W CRPS Titanium → 9.6 kW redundant output | [I] | M1
CG480-S5063 | Operating temperature 0-35 °C | [I] | M1
CG290-S3063 | PSU configuration not captured | [U]

## 4_Power_Budget
4 · Node power budget and rack fit (live model)
Blue-on-yellow cells are inputs. Component load is compared with PSU OUTPUT capacity in redundant mode; AC input and rack fit use PSU efficiency. Replace [U] inputs with OEM calculator output before any facility commitment.
Input | Unit | CG480 · 8× H200 NVL · 4× 3200 W (3+1) | CG290 · 4× H200 NVL · PSU unpublished | Tag | Basis
System |  | CG480-S5063 | CG290-S3063
GPUs installed | count | 8 | 4 | [I] | OEM max / scenario choice
GPU max power | W | 600 | 600 | [I] | NVIDIA / OEM GPU TDP
CPUs | count | 2 | 1 | [I] | OEM spec
CPU TDP | W | 350 | 350 | [U] | Scenario SKU choice - see 5_Host_CPU_Map
DIMMs | count | 32 | 16 | [U] | Scenario choice (max per 1_System_Spec)
Power per DDR5 RDIMM | W | 10 | 10 | [U] | Planning assumption; replace with OEM calculator
Data drives (NVMe) | count | 8 | 4 | [U] | Scenario choice
Power per data drive | W | 20 | 25 | [U] | Planning assumption: Gen5 U.2/E3.S ≈25 W, E1.S ≈20 W
Boot drives (M.2) | count | 0 | 2 | [I] | OEM spec
Power per boot drive | W | 8 | 8 | [U] | Planning assumption
Add-in NICs / DPUs | count | 5 | 3 | [U] | Scenario choice (N-S and/or E-W add-in)
Power per NIC / DPU | W | 25 | 25 | [U] | Planning assumption: CX-7 class ≈25 W; BlueField-3 ≈75 W
Baseboard / PCIe switch / NVSwitch / on-board CX-8 overhead | W | 250 | 150 | [U] | Planning placeholder - largest uncertainty on HGX nodes
Fans, VRs and conversion overhead | % of component load | 8% | 8% | [U] | Planning assumption
PSU efficiency at operating load | fraction | 0.95 | 0.95 | [U] | 80 PLUS Titanium ≈94-96% (HPE states up to 96%)
PSU output rating at site input voltage (0 = unpublished) | W | 3200 | 0 | [I] / [U] | OEM spec
PSUs installed | count | 4 | 0 | [I] / [U] | OEM spec / scenario
PSUs held for redundancy | count | 1 | 0 | [I] / [U] | N+1 = 1, N+N = half
PSUs in dedicated GPU power domain (0 = not modelled) | count | 0 | 0 | [I] | HPE DL380a only
Rack power budget | kW | 30 | 30 | [U] | Your facility figure
Node height | RU | 4 | 2 | [I] | OEM spec
Usable rack units for compute | RU | 38 | 38 | [U] | 42U minus ToR, PDU, patch
Outputs (formulas)
Output | Unit | CG480 · 8× H200 NVL · 4× 3200 W (3+1) | CG290 · 4× H200 NVL · PSU unpublished | Tag | Formula basis
GPU load | W | 4800 | 2400 | [D] | GPUs × GPU W
CPU load | W | 700 | 350 | [D] | CPUs × TDP
Memory load | W | 320 | 160 | [D] | DIMMs × W
Storage load | W | 160 | 116 | [D] | drives × W + boot × W
Network add-in load | W | 125 | 75 | [D] | NICs × W
Baseboard / switch overhead | W | 250 | 150 | [D] | input
Component subtotal | W | 6355 | 3251 | [D] | sum of above
Fans / VR / conversion | W | 508.4 | 260.08 | [D] | subtotal × %
Estimated max DC load | W | 6863.4 | 3511.08 | [D] | subtotal + fans
GPU share of DC load | % | 69.94% | 68.36% | [D] | GPU ÷ DC
Estimated max AC input | W | 7224.6316 | 3695.8737 | [D] | DC ÷ efficiency
PSU output in redundant mode | W | 9600 | n/a | [D] | (installed − redundant) × rating
Headroom (redundant) | W | 2736.6 | n/a | [D] | capacity − DC load
PSU utilisation (redundant) | % | 71.49% | n/a | [D] | DC ÷ capacity
Redundancy check |  | OK within redundant capacity | PSU data not published | [D]
GPU-domain PSU output (no domain redundancy) | W | n/a | n/a | [D] | GPU-domain PSUs × rating
GPU-domain check |  | n/a | n/a | [D] | GPU load ≤ domain output
Heat load | BTU/hr | 24650.4429 | 12610.321 | [D] | AC W × 3.412
AC power per GPU (all-in) | kW | 0.90308 | 0.92397 | [D] | AC ÷ GPUs
Nodes per rack - power limited | count | 4 | 8 | [D] | rack W ÷ node AC
Nodes per rack - space limited | count | 9 | 19 | [D] | usable RU ÷ node RU
Nodes per rack | count | 4 | 8 | [D] | min(power, space)
GPUs per rack | count | 32 | 32 | [D] | nodes × GPUs
Rack AC load at that fit | kW | 28.8985 | 29.567 | [D] | nodes × AC
Estimate is a planning ceiling at nameplate GPU/CPU power, not a measured draw. Sustained inference typically runs below nameplate; training and burn-in approach it. PSU ratings are OUTPUT watts at the stated input voltage - check derates (e.g., Dell 3200 W → 2900 W at 200-220 VAC; Lenovo 3200 W is 230 V-only).

## 5_Host_CPU_Map
5 · Host CPU map against the Xeon 6 SKU workbook
Rows 71-82 of 'SKU Recommendations' (GPU host CPU). Socket is the first filter; OEM qualified list the second.
CG480-S5063 — socket LGA-4710 (Socket E2); series Xeon 6700E / 6500P / 6700P
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
CG480-S5063 | Row 71 | Training | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 72 | Training | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 73 | Training | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
CG480-S5063 | Row 74 | Training | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 75 | Training | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
CG480-S5063 | Row 76 | Training | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 77 | Inference | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 78 | Inference | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 79 | Inference | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
CG480-S5063 | Row 80 | Inference | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
CG480-S5063 | Row 81 | Inference | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
CG480-S5063 | Row 82 | Inference | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
CG290-S3063 — socket (single Xeon 6 - socket unverified); series Xeon 6 (1S)
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
CG290-S3063 | Row 71 | Training | Good | 6747P | 48C/330W | Socket unverified | [U]
CG290-S3063 | Row 72 | Training | Good | 6732P | 32C/350W | Socket unverified | [U]
CG290-S3063 | Row 73 | Training | Better | 6960P | 72C/500W | Socket unverified | [U]
CG290-S3063 | Row 74 | Training | Better | 6767P | 64C/350W | Socket unverified | [U]
CG290-S3063 | Row 75 | Training | Best | 6962P* | 72C/500W | Socket unverified | [U]
CG290-S3063 | Row 76 | Training | Best | 6776P* | 64C/350W | Socket unverified | [U]
CG290-S3063 | Row 77 | Inference | Good | 6747P | 48C/330W | Socket unverified | [U]
CG290-S3063 | Row 78 | Inference | Good | 6732P | 32C/350W | Socket unverified | [U]
CG290-S3063 | Row 79 | Inference | Better | 6960P | 72C/500W | Socket unverified | [U]
CG290-S3063 | Row 80 | Inference | Better | 6767P | 64C/350W | Socket unverified | [U]
CG290-S3063 | Row 81 | Inference | Best | 6962P* | 72C/500W | Socket unverified | [U]
CG290-S3063 | Row 82 | Inference | Best | 6776P* | 64C/350W | Socket unverified | [U]

## Open_Questions
Risks and open questions
Items that change a planning number when resolved. Re-verify before any bid.
# | Open item | Why it matters | Resolve by
1 | CG290-S3063 PSU and socket | Cannot close the 2U power budget | MSI CG290-S3063 spec sheet
2 | Per-DIMM, per-drive, per-NIC and fan power are planning assumptions [U] | Non-GPU load is 15-30% of node power | OEM power calculators: HPE Power Advisor, Dell EIPT, Lenovo Capacity Planner, Supermicro/MSI sales tools
3 | Workbook CPU SKUs 6960P / 6962P (rows 73, 75, 79, 81) are LGA-7529 | Not installable in LGA-4710 GPU chassis - only 6900P platforms (SYS-522GA-NRT, XE9780LAP) | Adopt socket as first filter in capacity planner

## Sources
Sources
Every [I]/[3P] row in this workbook cites one of these IDs. Internal companion files are marked Internal.
ID | Source | Location | Class
M1 | MSI - CG480-S5063 specification sheet (Version D, 14 Jul 2026) | https://download-2.msi.com/archive/mnu_exe/server/CG480-S5063-Version-D07142026.pdf | [I]
M2 | MSI - CG480-S5063 product page | https://eps.msi.com/en/product/barebones/S5063G480RAE20 | [I]
M3 | MSI - RTX PRO Server lineup press release (26 Aug 2025) | https://www.msi.com/news/detail/MSI-Expands-NVIDIA-RTX-PRO-Server-Lineup---Accelerated-by-RTX-PRO-6000-Blackwell-Server-Edition-GPU-146930 | [I]
M4 | MSI - NVIDIA MGX landing page | https://www.msi.com/Landing/NVIDIA-MGX | [I]
M5 | MSI - CG480-S5063 Quick Start Guide | https://download-2.msi.com/archive/mnu_exe/server/S405-CG480-S5063-v1.0-QG.pdf | [I]
X5 | Internal - Intel_Xeon6_Workload_SKU_Recommendations.xlsx, sheet 'SKU Recommendations' rows 71-86 | Intel_Xeon6_Workload_SKU_Recommendations.xlsx | [I]

## Planner_YAML
Capacity-planner parameters (YAML)
Machine-readable block for Agentic Systems Capacity Planner ingestion. One line per row; copy column A verbatim.
system_option:
file: MSI_H200-NVL.xlsx
oem: MSI
gpu: H200-NVL
tier: "Mid-range (HBM/NVLink)"
chassis:
- model: "CG480-S5063"
rack_units: 4
cpu_socket: "LGA-4710 (Socket E2)"
- model: "CG290-S3063"
rack_units: 2
cpu_socket: "(single Xeon 6 - socket unverified)"
power_scenarios: # inputs only; outputs live in 4_Power_Budget
- name: "CG480 · 8× H200 NVL · 4× 3200 W (3+1)"
system: "CG480-S5063"
gpus: 8
gpu_w: 600
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 3200, installed: 4, redundant: 1}
assumptions_u: {dimm_w: 10, drive_w: 20, nic_w: 25, baseboard_w: 250, fan_pct: 0.08, psu_eff: 0.95}
- name: "CG290 · 4× H200 NVL · PSU unpublished"
system: "CG290-S3063"
gpus: 4
gpu_w: 600
cpu: {count: 1, tdp_w: 350}
psu: {rating_w: 0, installed: 0, redundant: 0}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 150, fan_pct: 0.08, psu_eff: 0.95}
compiled: "25 September 2026"