## Cover
Supermicro × NVIDIA HGX B300 — System Reference
OEM system options for the High-end tier · Xeon 6-hosted designs · Compiled 25 September 2026
Attribute | Value | Tag | Source
GPU | NVIDIA HGX B300 | [I]
Tier | High-end | [D]
System(s) | SYS-822GS-NB3RT | [I]
Host socket / series | SYS-822GS-NB3RT: LGA-4710 (Socket E2) (Xeon 6700P (P-cores)) | [D]
GPU silicon reference | NVIDIA_B300_Reference.xlsx | [D]
Host CPU reference | Intel_Xeon6_Workload_SKU_Recommendations.xlsx rows 71-82 (see 5_Host_CPU_Map) | [I] | X5
Cross-OEM comparison | NVIDIA_Enterprise_GPU_Index.xlsx | [D]
POSITIONING
Supermicro's air-cooled Xeon HGX B300 (8U) with published 3+3 × 6600 W — the most power headroom of the air-cooled B300 nodes here. A Gold Series build ships in 24 h per Supermicro.
Power at a glance (live links to 4_Power_Budget)
Scenario | Est. max DC load (W) | PSU redundant output (W) | Status
8× B300 · 6× 6600 W (3+3) | 12150.6 | 19800 | OK within redundant capacity
Provenance discipline
Tag | Meaning | Confidence | Use in planning
[I] | Vendor-published (NVIDIA datasheet/product page, OEM spec sheet, QuickSpecs, product guide) | High | Plan against
[D] | Derived here by stated arithmetic from [I] values (formula visible in cell) | Medium-High | Use; check formula
[3P] | Third-party measurement, reseller listing or press arithmetic | Medium | Cross-check before bid
[U] | Unpublished / unverified / planning assumption (editable input) | Low | Replace with OEM calculator output
[N] | Not applicable / not supported | - | -

## 1_System_Spec
1 · System specifications
One block per chassis. Conflicts between sources are shown side-by-side, not resolved silently.
SYS-822GS-NB3RT (Supermicro)
System | Section | Parameter | Value | Tag | Src
SYS-822GS-NB3RT | Identity | Model | Supermicro GPU SuperServer SYS-822GS-NB3RT (X14); Gold Series SYS-822GS-NB3RT-01-G2 | [I] | S1
SYS-822GS-NB3RT | Identity | Form factor | 8U rackmount, air-cooled, front I/O | [I] | S1
SYS-822GS-NB3RT | Processor | CPU | Dual Intel Xeon 6700 series with P-cores, ≤350 W TDP (store copy says 'up to 128 cores' - conflicts with 86C max for 6700P) | [I] | S1
SYS-822GS-NB3RT | Memory | Slots / max | 32 DDR5 RDIMM; up to 8 TB ECC DDR5-6400 (4 TB at 1 DPC 6400 / 8 TB at 2 DPC 5200 per sister B200 datasheet) | [I] | S1, S2
SYS-822GS-NB3RT | GPU | Complex | NVIDIA HGX B300 8-GPU, NVLink 5 1.8 TB/s, 2.3 TB HBM3e per system | [I] | S1
SYS-822GS-NB3RT | Network | E-W | 8× NVIDIA ConnectX-8 SuperNICs, up to 800 Gb/s (8× OSFP) | [I] | S1
SYS-822GS-NB3RT | Network | N-S / LAN | Up to two North/South NICs; 2× 10GbE RJ45; 1× dedicated BMC LAN | [I] | S1
SYS-822GS-NB3RT | Storage | Bays | 8× hot-swap E1.S NVMe; 2× M.2 NVMe | [I] | S1
SYS-822GS-NB3RT | Power | PSUs | 6× 6600 W redundant (3+3) Titanium | [I] | S1
SYS-822GS-NB3RT | Physical | Enclosure | 449 × 356 × 950 mm (17.6" × 13.8" × 37.4") | [I] | S1
SYS-822GS-NB3RT | Gold config | -01-G2 build | 2× Xeon '6768P' 64C 2.4 GHz (reseller; SKU name unverified), 2 TB DDR5-6400, 1× 960 GB M.2, 8-port 800G IB or 16-port 400GbE | [3P] | S6
SYS-822GS-NB3RT | Service | Onsite | Onsite service required | [I] | S1
SYS-822GS-NB3RT | This workbook | GPU population | NVIDIA HGX B300 — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]

## 2_Components
2 · Component and option list
Part / feature codes as published. Max qty is per system. Use for BOM drafting; confirm in OEM configurator.
System | Subsystem | Component | Part / feature code | Max qty | Spec | Tag | Src | Note
SYS-822GS-NB3RT | GPU | NVIDIA HGX B300 8-GPU board | onboard | 1 | 1100 W/GPU | [I] | S1
SYS-822GS-NB3RT | Network | ConnectX-8 SuperNIC 800G OSFP | onboard | 8 |  | [I] | S1
SYS-822GS-NB3RT | Power | 6600 W Titanium PSU |  | 6 | 3+3 | [I] | S1
SYS-822GS-NB3RT | Storage | E1.S NVMe |  | 8 |  | [I] | S1

## 3_Power_Rules
3 · OEM-published power and PSU rules
These constrain the scenarios on 4_Power_Budget. [U] rows are gaps to close with the OEM.
System | Rule | Tag | Src
SYS-822GS-NB3RT / -NBRT | 6× 6600 W Titanium, redundant 3+3 | [I] | S1, S2
SYS-822GS-NB3RT | Onsite service required | [I] | S1

## 4_Power_Budget
4 · Node power budget and rack fit (live model)
Blue-on-yellow cells are inputs. Component load is compared with PSU OUTPUT capacity in redundant mode; AC input and rack fit use PSU efficiency. Replace [U] inputs with OEM calculator output before any facility commitment.
Input | Unit | 8× B300 · 6× 6600 W (3+3) | Tag | Basis
System |  | SYS-822GS-NB3RT
GPUs installed | count | 8 | [I] | OEM max / scenario choice
GPU max power | W | 1100 | [I] | NVIDIA / OEM GPU TDP
CPUs | count | 2 | [I] | OEM spec
CPU TDP | W | 350 | [U] | Scenario SKU choice - see 5_Host_CPU_Map
DIMMs | count | 32 | [U] | Scenario choice (max per 1_System_Spec)
Power per DDR5 RDIMM | W | 10 | [U] | Planning assumption; replace with OEM calculator
Data drives (NVMe) | count | 8 | [U] | Scenario choice
Power per data drive | W | 20 | [U] | Planning assumption: Gen5 U.2/E3.S ≈25 W, E1.S ≈20 W
Boot drives (M.2) | count | 2 | [I] | OEM spec
Power per boot drive | W | 8 | [U] | Planning assumption
Add-in NICs / DPUs | count | 2 | [U] | Scenario choice (N-S and/or E-W add-in)
Power per NIC / DPU | W | 25 | [U] | Planning assumption: CX-7 class ≈25 W; BlueField-3 ≈75 W
Baseboard / PCIe switch / NVSwitch / on-board CX-8 overhead | W | 1000 | [U] | Planning placeholder - largest uncertainty on HGX nodes
Fans, VRs and conversion overhead | % of component load | 10% | [U] | Planning assumption
PSU efficiency at operating load | fraction | 0.95 | [U] | 80 PLUS Titanium ≈94-96% (HPE states up to 96%)
PSU output rating at site input voltage (0 = unpublished) | W | 6600 | [I] | OEM spec
PSUs installed | count | 6 | [I] | OEM spec / scenario
PSUs held for redundancy | count | 3 | [I] | N+1 = 1, N+N = half
PSUs in dedicated GPU power domain (0 = not modelled) | count | 0 | [I] | HPE DL380a only
Rack power budget | kW | 30 | [U] | Your facility figure
Node height | RU | 8 | [I] | OEM spec
Usable rack units for compute | RU | 38 | [U] | 42U minus ToR, PDU, patch
Outputs (formulas)
Output | Unit | 8× B300 · 6× 6600 W (3+3) | Tag | Formula basis
GPU load | W | 8800 | [D] | GPUs × GPU W
CPU load | W | 700 | [D] | CPUs × TDP
Memory load | W | 320 | [D] | DIMMs × W
Storage load | W | 176 | [D] | drives × W + boot × W
Network add-in load | W | 50 | [D] | NICs × W
Baseboard / switch overhead | W | 1000 | [D] | input
Component subtotal | W | 11046 | [D] | sum of above
Fans / VR / conversion | W | 1104.6 | [D] | subtotal × %
Estimated max DC load | W | 12150.6 | [D] | subtotal + fans
GPU share of DC load | % | 72.42% | [D] | GPU ÷ DC
Estimated max AC input | W | 12790.1053 | [D] | DC ÷ efficiency
PSU output in redundant mode | W | 19800 | [D] | (installed − redundant) × rating
Headroom (redundant) | W | 7649.4 | [D] | capacity − DC load
PSU utilisation (redundant) | % | 61.37% | [D] | DC ÷ capacity
Redundancy check |  | OK within redundant capacity | [D]
GPU-domain PSU output (no domain redundancy) | W | n/a | [D] | GPU-domain PSUs × rating
GPU-domain check |  | n/a | [D] | GPU load ≤ domain output
Heat load | BTU/hr | 43639.8392 | [D] | AC W × 3.412
AC power per GPU (all-in) | kW | 1.5988 | [D] | AC ÷ GPUs
Nodes per rack - power limited | count | 2 | [D] | rack W ÷ node AC
Nodes per rack - space limited | count | 4 | [D] | usable RU ÷ node RU
Nodes per rack | count | 2 | [D] | min(power, space)
GPUs per rack | count | 16 | [D] | nodes × GPUs
Rack AC load at that fit | kW | 25.5802 | [D] | nodes × AC
Estimate is a planning ceiling at nameplate GPU/CPU power, not a measured draw. Sustained inference typically runs below nameplate; training and burn-in approach it. PSU ratings are OUTPUT watts at the stated input voltage - check derates (e.g., Dell 3200 W → 2900 W at 200-220 VAC; Lenovo 3200 W is 230 V-only).

## 5_Host_CPU_Map
5 · Host CPU map against the Xeon 6 SKU workbook
Rows 71-82 of 'SKU Recommendations' (GPU host CPU). Socket is the first filter; OEM qualified list the second.
SYS-822GS-NB3RT — socket LGA-4710 (Socket E2); series Xeon 6700P (P-cores)
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
SYS-822GS-NB3RT | Row 71 | Training | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 72 | Training | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 73 | Training | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
SYS-822GS-NB3RT | Row 74 | Training | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 75 | Training | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
SYS-822GS-NB3RT | Row 76 | Training | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 77 | Inference | Good | 6747P | 48C/330W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 78 | Inference | Good | 6732P | 32C/350W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 79 | Inference | Better | 6960P | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
SYS-822GS-NB3RT | Row 80 | Inference | Better | 6767P | 64C/350W | Socket-compatible; OEM qualification unverified | [U]
SYS-822GS-NB3RT | Row 81 | Inference | Best | 6962P* | 72C/500W | Not installable - 6900P is LGA-7529 | [D]
SYS-822GS-NB3RT | Row 82 | Inference | Best | 6776P* | 64C/350W | Socket-compatible; OEM qualification unverified | [U]

## Open_Questions
Risks and open questions
Items that change a planning number when resolved. Re-verify before any bid.
# | Open item | Why it matters | Resolve by
1 | 'Up to 128 cores' in store copy vs 86C 6700P max | Host CPU qualification | Supermicro datasheet CPU list
2 | Gold config CPU '6768P' not an Intel SKU in the workbook | Could be a Supermicro-specific or mis-typed SKU | Supermicro Gold Series BOM
3 | Per-DIMM, per-drive, per-NIC and fan power are planning assumptions [U] | Non-GPU load is 15-30% of node power | OEM power calculators: HPE Power Advisor, Dell EIPT, Lenovo Capacity Planner, Supermicro/MSI sales tools
4 | Workbook CPU SKUs 6960P / 6962P (rows 73, 75, 79, 81) are LGA-7529 | Not installable in LGA-4710 GPU chassis - only 6900P platforms (SYS-522GA-NRT, XE9780LAP) | Adopt socket as first filter in capacity planner

## Sources
Sources
Every [I]/[3P] row in this workbook cites one of these IDs. Internal companion files are marked Internal.
ID | Source | Location | Class
S1 | Supermicro - SYS-822GS-NB3RT datasheet / eStore | https://www.supermicro.com/en/products/system/datasheet/sys-822gs-nb3rt | [I]
S2 | Supermicro - SYS-822GS-NBRT datasheet (HGX B200) | https://www.supermicro.com/en/products/system/datasheet/sys-822gs-nbrt | [I]
S6 | Wiredzone - SYS-822GS-NB3RT-01-G2 / SYS-522GA-NRT listings | https://www.wiredzone.com/shop/product/10034109-supermicro-sys-822gs-nb3rt-01-g2-hgx-b300-8-gpu-system-16806 | [3P]
X5 | Internal - Intel_Xeon6_Workload_SKU_Recommendations.xlsx, sheet 'SKU Recommendations' rows 71-86 | Intel_Xeon6_Workload_SKU_Recommendations.xlsx | [I]

## Planner_YAML
Capacity-planner parameters (YAML)
Machine-readable block for Agentic Systems Capacity Planner ingestion. One line per row; copy column A verbatim.
system_option:
file: Supermicro_B300.xlsx
oem: Supermicro
gpu: B300
tier: "High-end"
chassis:
- model: "SYS-822GS-NB3RT"
rack_units: 8
cpu_socket: "LGA-4710 (Socket E2)"
power_scenarios: # inputs only; outputs live in 4_Power_Budget
- name: "8× B300 · 6× 6600 W (3+3)"
system: "SYS-822GS-NB3RT"
gpus: 8
gpu_w: 1100
cpu: {count: 2, tdp_w: 350}
psu: {rating_w: 6600, installed: 6, redundant: 3}
assumptions_u: {dimm_w: 10, drive_w: 20, nic_w: 25, baseboard_w: 1000, fan_pct: 0.1, psu_eff: 0.95}
compiled: "25 September 2026"