## Cover
Supermicro × NVIDIA RTX PRO 4500 BSE — System Reference
OEM system options for the Entry tier · Xeon 6-hosted designs · Compiled 25 September 2026
Attribute | Value | Tag | Source
GPU | NVIDIA RTX PRO 4500 BSE | [I]
Tier | Entry | [D]
System(s) | SYS-522GA-NRT | [I]
Host socket / series | SYS-522GA-NRT: LGA-7529 (Socket BR) (Xeon 6900P (P-cores)) | [D]
GPU silicon reference | NVIDIA_RTX-PRO-4500_Reference.xlsx | [D]
Host CPU reference | Intel_Xeon6_Workload_SKU_Recommendations.xlsx rows 71-82 (see 5_Host_CPU_Map) | [I] | X5
Cross-OEM comparison | NVIDIA_Enterprise_GPU_Index.xlsx | [D]
POSITIONING
Supermicro's datasheet names RTX PRO 4500 BSE for SYS-522GA-NRT (10 single-width). A 6900P host is oversized for an entry GPU; treat as a mixed CPU-heavy + light-GPU node.
Power at a glance (live links to 4_Power_Budget)
Scenario | Est. max DC load (W) | PSU redundant output (W) | Status
10× RTX PRO 4500 (SW max) · 6× 2700 W (3+3 assumed) | 3678.48 | 8100 | OK within redundant capacity
Provenance discipline
Tag | Meaning | Confidence | Use in planning
[I] | Vendor-published (NVIDIA datasheet/product page, OEM spec sheet, QuickSpecs, product guide) | High | Plan against
[D] | Derived here by stated arithmetic from [I] values (formula visible in cell) | Medium-High | Use; check formula
[3P] | Third-party measurement, reseller listing or press arithmetic | Medium | Cross-check before bid
[U] | Unpublished / unverified / planning assumption (editable input) | Low | Replace with OEM calculator output
[N] | Not applicable / not supported | - | -

## 1_System_Spec
1 · System specifications
One block per chassis. Conflicts between sources are shown side-by-side, not resolved silently.
SYS-522GA-NRT (Supermicro)
System | Section | Parameter | Value | Tag | Src
SYS-522GA-NRT | Identity | Model | Supermicro GPU SuperServer SYS-522GA-NRT (X14; chassis CSE-528G2TS-R5K40P, board X14DBG-AP) | [I] | S3, S6
SYS-522GA-NRT | Identity | Form factor | 5U rackmount, dual-root PCIe | [I] | S3
SYS-522GA-NRT | Processor | CPU | Dual Intel Xeon 6900 series P-cores, up to 128C/256T, up to 504 MB cache, ≤500 W (air); Socket BR LGA-7529 | [I] | S3
SYS-522GA-NRT | Memory | Slots / max | 24 DIMM; up to 6 TB DDR5-6400 RDIMM or DDR5-8800 MRDIMM (1 DPC) | [I] | S3
SYS-522GA-NRT | GPU | Capacity | Up to 8 double-width or 10 single-width GPUs; PCIe 5.0 x16 switch, dual-root; optional NVLink bridge | [I] | S3
SYS-522GA-NRT | GPU | Supported NVIDIA | RTX PRO 4500 BSE, RTX PRO 6000 BSE (datasheet); H200 NVL (EU eStore) | [I] | S3
SYS-522GA-NRT | Expansion | Slots | Up to 13 PCIe 5.0 x16 FHFL | [3P] | S6
SYS-522GA-NRT | Storage | Bays | 24× front hot-swap 2.5" PCIe 5.0 NVMe; 2× M.2 NVMe | [I] | S3
SYS-522GA-NRT | Network | LAN | 2× RJ45 10GbE | [I] | S3
SYS-522GA-NRT | Power | PSUs | 6× 2700 W redundant Titanium | [I] | S3
SYS-522GA-NRT | Power | Rack reference | 4-node rack at 36.6 kW (SYS-522GA-TNR variant, RTX PRO 6000 AI Factory datasheet) | [I] | S5
SYS-522GA-NRT | Cooling | Fans | 10 heavy-duty PWM fans with air shroud | [I] | S3
SYS-522GA-NRT | Physical | Enclosure | 438 × 222.5 × 786.1 mm (17.2" × 8.75" × 31") | [I] | S3
SYS-522GA-NRT | Security | Features | TPM 2.0, Secure Boot, NIST 800-193 Silicon RoT, signed firmware, system lockdown | [I] | S3
SYS-522GA-NRT | This workbook | GPU population | NVIDIA RTX PRO 4500 BSE — max per chassis per GPU config rows above; power scenarios on 4_Power_Budget | [D]

## 2_Components
2 · Component and option list
Part / feature codes as published. Max qty is per system. Use for BOM drafting; confirm in OEM configurator.
System | Subsystem | Component | Part / feature code | Max qty | Spec | Tag | Src | Note
SYS-522GA-NRT | Power | 2700 W Titanium PSU |  | 6 |  | [I] | S3
SYS-522GA-NRT | Storage | 2.5" PCIe 5.0 NVMe |  | 24 |  | [I] | S3
SYS-522GA-NRT | Memory | DDR5 RDIMM / MRDIMM |  | 24 | 6400 / 8800 | [I] | S3

## 3_Power_Rules
3 · OEM-published power and PSU rules
These constrain the scenarios on 4_Power_Budget. [U] rows are gaps to close with the OEM.
System | Rule | Tag | Src
SYS-522GA-NRT | 6× 2700 W Titanium; redundancy scheme not stated in retrieved sources | [I] | S3
SYS-522GA-NRT | Supermicro RTX PRO 6000 AI Factory reference: 4 nodes per rack at 36.6 kW (≈9.15 kW/node) - above a 3+3 × 2700 W = 8.1 kW envelope, implying N+1-class operation at full load | [D] | S5

## 4_Power_Budget
4 · Node power budget and rack fit (live model)
Blue-on-yellow cells are inputs. Component load is compared with PSU OUTPUT capacity in redundant mode; AC input and rack fit use PSU efficiency. Replace [U] inputs with OEM calculator output before any facility commitment.
Input | Unit | 10× RTX PRO 4500 (SW max) · 6× 2700 W (3+3 assumed) | Tag | Basis
System |  | SYS-522GA-NRT
GPUs installed | count | 10 | [I] | OEM max / scenario choice
GPU max power | W | 165 | [I] | NVIDIA / OEM GPU TDP
CPUs | count | 2 | [I] | OEM spec
CPU TDP | W | 500 | [U] | Scenario SKU choice - see 5_Host_CPU_Map
DIMMs | count | 24 | [U] | Scenario choice (max per 1_System_Spec)
Power per DDR5 RDIMM | W | 10 | [U] | Planning assumption; replace with OEM calculator
Data drives (NVMe) | count | 8 | [U] | Scenario choice
Power per data drive | W | 25 | [U] | Planning assumption: Gen5 U.2/E3.S ≈25 W, E1.S ≈20 W
Boot drives (M.2) | count | 2 | [I] | OEM spec
Power per boot drive | W | 8 | [U] | Planning assumption
Add-in NICs / DPUs | count | 2 | [U] | Scenario choice (N-S and/or E-W add-in)
Power per NIC / DPU | W | 25 | [U] | Planning assumption: CX-7 class ≈25 W; BlueField-3 ≈75 W
Baseboard / PCIe switch / NVSwitch / on-board CX-8 overhead | W | 250 | [U] | Planning placeholder - largest uncertainty on HGX nodes
Fans, VRs and conversion overhead | % of component load | 8% | [U] | Planning assumption
PSU efficiency at operating load | fraction | 0.95 | [U] | 80 PLUS Titanium ≈94-96% (HPE states up to 96%)
PSU output rating at site input voltage (0 = unpublished) | W | 2700 | [I] | OEM spec
PSUs installed | count | 6 | [I] | OEM spec / scenario
PSUs held for redundancy | count | 3 | [U] | N+1 = 1, N+N = half
PSUs in dedicated GPU power domain (0 = not modelled) | count | 0 | [I] | HPE DL380a only
Rack power budget | kW | 30 | [U] | Your facility figure
Node height | RU | 5 | [I] | OEM spec
Usable rack units for compute | RU | 38 | [U] | 42U minus ToR, PDU, patch
Outputs (formulas)
Output | Unit | 10× RTX PRO 4500 (SW max) · 6× 2700 W (3+3 assumed) | Tag | Formula basis
GPU load | W | 1650 | [D] | GPUs × GPU W
CPU load | W | 1000 | [D] | CPUs × TDP
Memory load | W | 240 | [D] | DIMMs × W
Storage load | W | 216 | [D] | drives × W + boot × W
Network add-in load | W | 50 | [D] | NICs × W
Baseboard / switch overhead | W | 250 | [D] | input
Component subtotal | W | 3406 | [D] | sum of above
Fans / VR / conversion | W | 272.48 | [D] | subtotal × %
Estimated max DC load | W | 3678.48 | [D] | subtotal + fans
GPU share of DC load | % | 44.86% | [D] | GPU ÷ DC
Estimated max AC input | W | 3872.0842 | [D] | DC ÷ efficiency
PSU output in redundant mode | W | 8100 | [D] | (installed − redundant) × rating
Headroom (redundant) | W | 4421.52 | [D] | capacity − DC load
PSU utilisation (redundant) | % | 45.41% | [D] | DC ÷ capacity
Redundancy check |  | OK within redundant capacity | [D]
GPU-domain PSU output (no domain redundancy) | W | n/a | [D] | GPU-domain PSUs × rating
GPU-domain check |  | n/a | [D] | GPU load ≤ domain output
Heat load | BTU/hr | 13211.5513 | [D] | AC W × 3.412
AC power per GPU (all-in) | kW | 0.38721 | [D] | AC ÷ GPUs
Nodes per rack - power limited | count | 7 | [D] | rack W ÷ node AC
Nodes per rack - space limited | count | 7 | [D] | usable RU ÷ node RU
Nodes per rack | count | 7 | [D] | min(power, space)
GPUs per rack | count | 70 | [D] | nodes × GPUs
Rack AC load at that fit | kW | 27.1046 | [D] | nodes × AC
Estimate is a planning ceiling at nameplate GPU/CPU power, not a measured draw. Sustained inference typically runs below nameplate; training and burn-in approach it. PSU ratings are OUTPUT watts at the stated input voltage - check derates (e.g., Dell 3200 W → 2900 W at 200-220 VAC; Lenovo 3200 W is 230 V-only).

## 5_Host_CPU_Map
5 · Host CPU map against the Xeon 6 SKU workbook
Rows 71-82 of 'SKU Recommendations' (GPU host CPU). Socket is the first filter; OEM qualified list the second.
SYS-522GA-NRT — socket LGA-7529 (Socket BR); series Xeon 6900P (P-cores)
System | Workbook row | Workload | Tier | SKU | Cores/TDP | Status | Tag
SYS-522GA-NRT | Row 71 | Training | Good | 6747P | 48C/330W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 72 | Training | Good | 6732P | 32C/350W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 73 | Training | Better | 6960P | 72C/500W | Socket-compatible (6900P); OEM qualification unverified | [U]
SYS-522GA-NRT | Row 74 | Training | Better | 6767P | 64C/350W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 75 | Training | Best | 6962P* | 72C/500W | Socket-compatible (6900P); OEM qualification unverified | [U]
SYS-522GA-NRT | Row 76 | Training | Best | 6776P* | 64C/350W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 77 | Inference | Good | 6747P | 48C/330W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 78 | Inference | Good | 6732P | 32C/350W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 79 | Inference | Better | 6960P | 72C/500W | Socket-compatible (6900P); OEM qualification unverified | [U]
SYS-522GA-NRT | Row 80 | Inference | Better | 6767P | 64C/350W | Not installable - 6700P is LGA-4710 | [D]
SYS-522GA-NRT | Row 81 | Inference | Best | 6962P* | 72C/500W | Socket-compatible (6900P); OEM qualification unverified | [U]
SYS-522GA-NRT | Row 82 | Inference | Best | 6776P* | 64C/350W | Not installable - 6700P is LGA-4710 | [D]

## Open_Questions
Risks and open questions
Items that change a planning number when resolved. Re-verify before any bid.
# | Open item | Why it matters | Resolve by
1 | SYS-522GA-NRT PSU redundancy (3+3 vs N+1) | 3+3 caps the node at 8.1 kW output - the scenarios show whether an 8-GPU build fits | Supermicro datasheet power section / sales engineering
2 | Per-DIMM, per-drive, per-NIC and fan power are planning assumptions [U] | Non-GPU load is 15-30% of node power | OEM power calculators: HPE Power Advisor, Dell EIPT, Lenovo Capacity Planner, Supermicro/MSI sales tools
3 | Workbook CPU SKUs 6960P / 6962P (rows 73, 75, 79, 81) are LGA-7529 | Not installable in LGA-4710 GPU chassis - only 6900P platforms (SYS-522GA-NRT, XE9780LAP) | Adopt socket as first filter in capacity planner

## Sources
Sources
Every [I]/[3P] row in this workbook cites one of these IDs. Internal companion files are marked Internal.
ID | Source | Location | Class
S3 | Supermicro - SYS-522GA-NRT datasheet / eStore | https://www.supermicro.com/en/products/system/datasheet/sys-522ga-nrt | [I]
S5 | Supermicro - AI Factory with RTX PRO 6000 datasheet (rack power per 4 nodes) | https://www.supermicro.com/datasheet/Datasheet_Supermicro_NVIDIA_AI_Factories_RTX_PRO_6000.pdf | [I]
S6 | Wiredzone - SYS-822GS-NB3RT-01-G2 / SYS-522GA-NRT listings | https://www.wiredzone.com/shop/product/10034109-supermicro-sys-822gs-nb3rt-01-g2-hgx-b300-8-gpu-system-16806 | [3P]
X5 | Internal - Intel_Xeon6_Workload_SKU_Recommendations.xlsx, sheet 'SKU Recommendations' rows 71-86 | Intel_Xeon6_Workload_SKU_Recommendations.xlsx | [I]

## Planner_YAML
Capacity-planner parameters (YAML)
Machine-readable block for Agentic Systems Capacity Planner ingestion. One line per row; copy column A verbatim.
system_option:
file: Supermicro_RTX-PRO-4500.xlsx
oem: Supermicro
gpu: RTX-PRO-4500
tier: "Entry"
chassis:
- model: "SYS-522GA-NRT"
rack_units: 5
cpu_socket: "LGA-7529 (Socket BR)"
power_scenarios: # inputs only; outputs live in 4_Power_Budget
- name: "10× RTX PRO 4500 (SW max) · 6× 2700 W (3+3 assumed)"
system: "SYS-522GA-NRT"
gpus: 10
gpu_w: 165
cpu: {count: 2, tdp_w: 500}
psu: {rating_w: 2700, installed: 6, redundant: 3}
assumptions_u: {dimm_w: 10, drive_w: 25, nic_w: 25, baseboard_w: 250, fan_pct: 0.08, psu_eff: 0.95}
compiled: "25 September 2026"